309-Y / H05V2V2-F EN 50525-2-11 Heat Resistant Flex Cable
For internal wiring or supply cords to electrical apparatus, particularly for use in high temperature zones such as near central heating systems, near ovens or in industrial kitchens etc.
Flex Cable Specifications
- Voltage Rating: 300/500V
- Temperature Rating:
  - Flexed: +5°C to +90°C
- Minimum Bending Radius:
  - Fixed: 6 x overall diameter
  - Flexed: 10 x overall diameter
- Conductor: Class 5 flexible copper conductor
- Insulation: PVC (Polyvinyl Chloride)
- Sheath: PVC
- Core Identification:
  - 2 Core: Blue, Brown
  - 3 core: Green/Yellow, Blue, Brown
  - 4 core: Green/Yellow, Brown, Black, Grey
- Sheath Colour: White/Black
- Cables are tested and accredited by BASEC, The British Approvals Service for Cables
- British Standards: EN 50525-2-11, EN 60228 Flame Retardant according to IEC/EN 60332-1-2
Flex Cable Dimensions
Number of Cores	Nominal Cross Sectional Area (mm²)	Nominal Thickness of Insulation (mm)	Nominal Overall Diameter (mm)	Nominal Weight (Kg per km)
2	0.75	0.6	6.3	63
3	0.75	0.6	6.7	74
3	1	0.6	7	86
3	1.5	0.7	8.1	115
3	2.5	0.8	9.7	170
4	0.75	0.6	7.3	78
4	1	0.6	7.9	110
4	1.5	0.7	9	140
4	2.5	0.8	10.8	210
5	0.75	0.6	8.1	105

Conductors
Nominal Cross Sectional Area (mm²)	Maximum Diameter of Wires In Conductor (mm)	Maximum Resistance of Conductors at 20°C
0.75	0.21	26
1	0.21	19.5
1.5	0.26	13.3
2.5	0.26	7.98
4	0.31	4.95

Electrical Characteristics
Nominal Cross Sectional Area (mm²)	Current Carrying Capacity (Amps) Single Phase AC	Current Carrying Capacity (Amps) Three-Phase AC	Maximum Mass Supportable by Twin Flexible Cord
0.75	6	6	3
1	10	10	5
1.5	16	16	5
2.5	25	20	5

Voltage Drop
Nominal Cross Sectional Area (mm²)	DC or Single-Phase AC (mV/A/m)	Three-Phase AC (mV/A/m)
0.75	62	54
1	46	40
1.5	32	27
2.5	19	16

De-Rating Factors
Air Temperature	De-rating Factor
35°C	0.91
40°C	0.82
45°C	0.71
50°C	0.58
55°C	0.41